Our system consists of various manufacturers' instruments, and sometime we meet errors of unknown origin. Each manufacturer of the system says their part of system has no problem. Any idea?

Most of this kind of problems will be solved by installing isolator units (M-System model: M2VS, etc.) between each system. In addition, by installing isolator units, the responsibility of each manufacturer's system will be clarified easily.

Each manufacturer's instrument and system has each concept, therefore, it is matter of course that interactions may happen if these systems are connected directly without any isolator units between them. With isolator units installed, it is not necessary for you to consider interactions which could come from different systems.

In some cases, the whole system as total does not function properly even though each independent instrument is working correctly. There we have to consider noise influence on signal transmission lines. When there are machines operated by high voltage in the field, an AC common mode voltage (vs. ground) sometimes appears on the signal lines due to the magnetic field created by these machines. In case this common mode voltage is less than permissible value of the receiver instrument, the operation of the instrument becomes unstable. The simplest solution to prevent this common mode noise problem is to install an isolator unit on the signal transmission line.

