Can you tell us how to minimize a destruction of instruments at control room site caused by a field instrument trouble?

Installing Isolator Units between the field and control room does minimize such problems.

For example, a pump failure would trigger its safety valve and then high temperature/high pressure steam burst out, which melts covering of electrical wires. If the damaged signal lines and power lines are shorted, both field instruments and control room instruments would be destroyed.

It is matter of course to pay attention to separately wire power and signal transmission cables in advance, but sometimes it is simply not possible when you need to squeeze everything in a limited space.

Field site environment in general is poorer compared from control rooms because of existence of potential danger by high voltage, high temperature or high pressure. There are more possibilities of accidents.

An Isolator Unit isolates DC signals which pass through it and can withstand 2000V AC applied between insulated circuits for 1 minute. It separates galvanically sensors, transmitters, final control elements connected directly to field plants from control equipment in control rooms. This will prevent damage expansion to the control rooms in case of a plant accident. 