It is said that the grounding at two locations would cause errors. Why? How can I handle the problem?

When you ground at two locations, you could create a ground loop through which a current is transmitted from one instrument to another and added to the signal. This problem can be solved by installing an isolator between them.

In the electric world, the ground is a stable standard which most instrumentation uses as a reference point. We sometimes observe a spark between a hand and a doorknob which, isolated from the ground, is charged with high potential. This much of high potential could destroy semiconductors.

A stable system means that it is not isolated from the ground, and that the power lines and signal lines are referenced to the ground potential. However, a minute difference in the ground potentials could cause an error in an instrumentation system handling several volts as the full-scale.

It is common for the ground terminal of an instrumentation panel to which many instruments are connected has a potential difference. If a signal line is grounded at two points which have different potentials, a current flow created by this difference is added to the signal current.

Now if you have an isolator between these two instruments, each ground point is galvanically separated. You can also choose any grounding point ideal for each instrument (typically where it is installed.)

