During a recent lightning storm, the power was turned off but some instruments were still damaged. Can you explain this?

Lightning jumped across the single-pole switch into the instrumentation. We would recommend to use a double-pole switch. However, this does not insure that a severe lightning surge will not damage it depending on the insulation resistance of the switch or the size of the lightning pulse. The only sure solution is to install a lightning surge protector in line with the power source.

| - Single-pole switch |  |  |
| --- | --- | --- |
| - Double-pole switch |  |  |
| Model | Function & Features |  |
| MDP-24-1 | 4-20mA DC & Pulse signal lines |  |
| MDM2A-24 | 4-20mA DC & Pulse signal lines with Life monitor function |  |
| MDPA-24 | 4-20mA DC & Pulse signal lines with Life monitor function and degradation checker |  |
| MA-100 / 200 | Power supply lines 100-120V or 200-240V AC; 2A |  |
| MAX-100 / 200 | Power supply lines 100-120V or 200-240V AC; 5A |  |
| MAA-100 / 200 | Power supply lines 100-120V or 200-240V AC with Life monitor function; 5A |  |
| MAAC-100 / 200 | Power supply lines 100-120V or 200-240V AC with Life monitor function and surge counter; 5A |  |

M-System has flexible solutions to meet your specific application and requirements. Consult our Signal Conditioners Data Library. 