I want to indicate an integrated flow value by 4 – 20mA DC analog signal output by a 2-wire electromagnetic flowmeter.

M-System’s DC/Frequency Converter and a totalizer realize your application. The DC/Frequency Converter (model: AP, APU) accepts an analog input and provides a pulse rate output in proportion to the input.

Let’s give an example how to indicate an integrated flow by an analog signal with flow range 0 – 400m3/h. First determine the volume per count to input to the totalizer. Now 0.1m3/h per count in this example. When the max. flow 400m3 flows for an hour, the pulse should be 4,000 pulses.  Therefore, the max. output frequency of the DC/Frequency Converter will be 4,000 pulses/h = 4,000 (pulses) / 3,600 (seconds) = 1.11111…. (Hz). Specify the output range 0 – 1.111Hz as effective digit of the DC/Frequency Converter is 4. Then the totalizer indicates this pulse signal.

Max. output frequency may be very small, e.g. 0.01666…. depending on the flow range or how to determine volume per count. However M-System’s DC/Frequency Converter can provide micro Hz output. In the above case, specify the output range 0 – 16.67mHz.

M-System has flexible solutions to meet your specific application and requirements. Consult our Signal Conditioners Data Library. 