What are the input waveform requirements when using average sensing vs. RMS sensing type current/voltage transducers?

Average sensing and RMS sensing type transducers have different characteristics for distorted input waveforms.

When making your selection, refer to the following table and verify your input waveform.

| SENSING TYPE | ACCURACY |
| --- | --- |
| Average | 3rd harmonic wave 15% : ±5% SCR waveform*: ±15% |
| RMS | 3rd harmonic wave 15%: ±0.2% SCR waveform*: ±0.5% |

*SCR (Silicon Controlled Rectifier) Waveform

It is recommended that you use the auxiliary-powered type transducers when the input signals have special waveform characteristics.

This is due to the fact that a self-powered transducer uses input signal voltage for driving its internal electronic circuitry. Special waveforms may not provide enough energy even when the signal level is within the described operational range.

M-System has flexible solutions to meet your specific application and requirements. Consult our Signal Conditioners Data Library. 