When one of the three input terminals (ex X3) is open because this input is reserved for future expansion system, will there be any problem? What I have to do?

My equation is as follows:

X0 = K0 {K1 (X1 + A1) + K2 (X2 + A2) + K3 (X3 + A3)} + A0

The default setting for K3, gain for input X3, equals one (1). In order to avoid problem, set the value for K3 to zero (0). Use the Programming Unit model PU-2A for setting.

With 4-20 mAdc input, 100Ω internal resistor is attached to each set of input terminals. If the K3 is set to one (1), the term “K3 (X3 + A3)” will be calculated in spite that there is no input X3: the JFK unit will calculate as if –25% input (0 mA for 4-20 mA span) is received.

With 1-5 Vdc input, input impedance is very high (≥ 1 MΩ). It is recommended to shortcircuit across these open terminals in order to prevent electrostatic induction.

M-System has flexible solutions to meet your specific application and requirements. Consult our Signal Conditioners Data Library. 