Voltage divider— Model M2VV

To monitor a solar power system, we measure an output voltage of its system and want to receive an alarm outputs if the measuring value fell than a set value. We had used a DC Alarm, model AS4V previously, but this time, the measuring voltage range is to be 0-1,000Vdc which is not able to input directly to the AS4V. Additionally, our existing panel room is not so large.

Do you have any good idea to solve our problem?

M-System recommends you to use a voltage divider, model M2VV. The maximum input range of the AS4V is -10V to +10Vdc so that you cannot input the solar power system generating power, 0 to 1,000Vdc to the AS4V directly. The M2VV can step down a voltage value by the dividing rate from 1/300 to 1/1000. In this case, please specify the dividing ratio 1/1,000. Through the voltage divider, the output of the M2VV will become to be 0 to 1Vdc, which will be easily acceptable value for the AS4V.
M2VV doesn’t need any auxiliary power and will be easily installed in a small panel space thanks to its small/ compact size.

Power of M
If input voltage is up to 600Vdc, isolators like M2VS, SV, KVS and etc. can be build with special specifications. Please contact M-System for details.

M-System has flexible solutions to meet your specific application and requirements. Consult our Signal Conditioners Data Library. 