PC Recorder — Model R1M

We have an application similar to the one on previous issue.  This one is a hotel with larger scale. They have 800 guest rooms and want to monitor the water flow from flowmeter at each room.  Is M-System PC recorder capable in handling this?

Yes, you still can use M-System R1M-P4 modules for your application.

R1M is a remote I/O module with Modbus communication feature with which you can form a local network for your monitoring system easily.  However, by Modbus standard the distance for this network is limited within 500 meters.

Now from the scale of your hotel, your network may be farther than this distance.  Still, in this case, you can expand the distance by grouping several R1M-P4 modules into a local network, and then using a 72EM to convert the Modbus protocol into Ethernet protocol and lead it to computer.

Another thing one may need to think about is the monitoring software.  As the free monitoring software MSR128 can only monitor up to 128 channels, it is not suitable for 800-room hotel.  But there are bunches of SCADA software from third party.  With the combination of SCADA software and our R1M I/O module, you can easily configure your own monitoring system.

M-System has flexible solutions to meet your specific application and requirements. Consult our Signal Conditioners Data Library. 