# Adding two flow signals from flowmeters

We are planning to add flow signals from two-flow meter. We’d like to use M-System model M2ADS but we have no idea how to determine each parameter K1 and K2.

We use 4-20 mA signals for all inputs and output. Power input will be 220 Vac.

Actual flow values are as follows: Input (1) 0 to 2.5 m3/h

Input (2) 0 to 7.5 m3/h

Output 0 to 10 m3/h

Could you advise how to determine each K1 and K2?

The thinking method of specifying parameter is as follows:

K1 & K2 will be specified as input actual flow span ratio in output actual flow span. In the above case, the actual flow span is specified [Max flow – Minimum flow].

We consider K1 and K2 as ratio in the output span and calculate them into the equation. In the case of M2ADS, the equation is as below:

Output = K1 x Input 1 + K2 x Input 2

When you use the output actual value span 10 m3/h as the base, each input ratio should be specified as follows:

Input 1 (K1) = (2.5 – 0) / (10 – 0) = 0.25

Input 2 (K2) = (7.5 – 0) / (10 – 0) = 0.75

That is K1 = 0.25 and K2 = 0.75

For example, if Input 1 is 12 mAdc then the input ratio is 0.5 and if Input 2 is 20 mAdc then the input ratio is 1.0, it means that Input 1 ratio is calculated as (12 – 4) / (20 – 4) and Input 2 ratio is calculated as (20 – 4) / (20 – 4)

In this case, the output will be calculated as below and the output ratio will be 0.875.

Output = K1 x 0.5 + K2 x 1.0

= 0.25 x 0.5 + 0.75 x 1.0

= 0.125 + 0.75

= 0.875

To convert 0.875 to output current value, then you can find it as 18 mAdc.

(X – 4) / (20 – 4) = 0.875

0.875 x 16 + 4 = 18 mAdc 