# Emergency Supervising at Control Room

We plan to monitor working situation of plant equipment at control room. When field equipment has working trouble, it will provide discrete status signal as working error and we’d like to check it at control room.

8 discrete signals will be required to monitor at the control room. The distance between the field equipment and the field panel is approx. 50 meters. Between the field panel and the control room is approx. 200 meters. We’d like to let the warning light on at both field panel end and control room end. Does M-System have any solution with low cost?

We'd like to recommend you to use our multi-transmission module 22LA1 for this application. Max. 500 meter transmission distance is available for multiple places with daisy chain manner.

In this case, please install Di 8-point unit (22LA1-3A4) at field equipment end and then Do 8-point unit (22LA1-3C7) is needed to install both at field panel end and control room end.

As for station number, please set it as same number (e.g. SA1: 0, SA2: 1) for each unit at each place. The same station number setting enables you to confirm the discrete in/out at each place at the same time.

We also recommend you to install lightning surge protector in order to protect the 22LA1. Recommended model is the MDP-DM3 for twisted-pair signal line and the MAA-100 for power input line.