# How to measure AC current and display the current level with the lamp

We are monitoring the power of a production line. Although the instantaneous power is already monitoring at the central monitor room, additionally we like to display rough value of current at site. Specifically, we want to classify the current values into three to four levels in advance and display the present current value with the corresponding lamp lit. We need to install measuring equipment easily without interrupting the facilities, and furthermore, we do not want to have the generated in-rush current at the time of starting the facilities indicated by the lamps. Is there any method to realize these requirements? The normal AC current is around 45 A and the maximum current is around 50 A.

M-System has a solution using the CLSC-10 Clamp AC Sensor and the AS4CT CT Digital Alarm. The CLSC is a clamp-type current sensor with an AC output of 0 to 1 A and can be mounted to hot lines. Furthermore, the CLSC incorporates an overvoltage clamp element, which ensures safety because no high voltage is generated if the output terminals are open. The AS4CT provides quad relay outputs at preset AC current levels from the CLSC. Originally, the AS4CT was developed as a comparator alarm. In your case, output contact signals as comparison results are combined to indicate the zone of the input signal classified by four set values (e.g., 40, 43, 47, and 50 A). The ON-delay time of the contact signals can be adjusted between 0 and 99 seconds so that the in-rush current will not be indicated.