# Wide power input-voltage DC alarm

We have a wheeled platform operated by 48V DC (connected 2 pcs. of 24V DC batteries in series).  The batteries are also used as 24V DC power supplies of the PLC and relays.  I want to get an alarm output when battery voltage drops to 20V DC.  However, usually a limit alarm module won’t function when its power supply drops to that level. Is there any suitable product for this case?

We propose DC alarm (model: M2AVS), of which operational power input voltage is 11 to 27V DC.  Its alarm output functions normal even if the batteries voltage drops 15% to 20V DC. 